## Input
INPUT DATA – Configuration and Parameters
Fill in blue fields. Guidance for solution choices, not definitive.
QUESTIONS | ANSWERS | GUIDANCE
1. LOCAL CONDITIONS – Communication
4G coverage at location? | No | Check Telenor coverage map
NB-IoT coverage at location? | No | Check Telenor coverage map
Line of sight < 15 km to base station? | No | Use a line-of-sight calculator, NKOM.no has a free web solution.
Two-way control required (remote-controlled valve)? | No | Two-way = requires 4G or satellite
2. FACILITY TYPE & RELEASE METHOD (NVE Ch. 3–5) |  | Concession terms determine release method and measurement technique
Release method (arrangement)? | Pipe via intake | NVE Guide 3/2020 Ch. 3–5. Incl. Coanda screens (Ch. 5.4)
Fish passage at intake? | Yes | NVE Ch. 5: Extra attraction water + up-/downstream migration
Required minimum flow (l/s)? | 20 | Specified in the concession (m³/s or l/s)
Low conductivity in water? | No | Pipe only: Yes = ultrasound, No = electromagnetic
Ice problems at measurement site? | No | NVE: Ice/sediment affects measurement profile and sensor selection
Difficult access to intake? | No | NVE Ch. 9: Affects logger backup and camera requirements
Linear flow at intended measurement site? | No | Pipe only: Air affects Doppler/ultrasound. Requires straight run.
Sediment or surge problem? | No | Yes = bubble tube recommended over pressure cell
3. OPERATIONS – Inspections & Autonomy |  | Determines logger redundancy and secondary source
Number of inspections/visits per year? | 4 | NVE: min. annual main inspection. ≤4 = 2 loggers. Must be a value between 3–30 days
Battery bank size (Ah) | 500 | Typically 100–500 Ah
Desired zero-emission (methanol)? | No | Yes = fuel cell, No = visit frequency determines diesel/methanol
TECHNICAL PARAMETERS
Solar Panel System
Parameter | Unit | Value | Comment
PV panel power | Wp | 425 | From the datasheet for selected panel
Number of panels | pcs | 2 | The configurator calculates this
System efficiency | % | 0.8 | Total system loss incl. cables, inverter, temperature. Typically 75–85%.
Expected lifespan in years | yr | 25 | Expected lifespan for PV panels
Battery Bank
Parameter | Unit | Value | Comment
Nominal voltage | V | 12.8 | System nominal voltage (12V or 24V)
Max depth of discharge (DoD) | factor (0–1) | 0.8 | LiFePO4: 80–90%, Lead-acid: 50%
Cycle lifespan | cycles | 6000 | LiFePO4: ~3000–6000, AGM: ~500–1200
Fuel Cell
Parameter | Unit | Value | Comment
Purchase cost | kr | 88000 | Purchase price excl./incl. VAT per supplier
Power | W | 82 | Nominal power from datasheet (W)
Fuel consumption | l/kWh | 0.9 | Methanol fuel consumption per kWh produced
Fuel price (methanol) | kr/l | 75 | Market price methanol per liter
Lifespan | hours | 6500 | Expected lifespan in operating hours
Annual maintenance cost | kr | 100 | Annual service/maintenance fuel cell
Diesel Generator
Parameter | Unit | Value | Comment
Purchase cost | kr | 35000 | Purchase price excl./incl. VAT per supplier
Power | W | 6500 | Nominal power from datasheet (W)
Fuel consumption | l/kWh | 0.5 | Diesel fuel consumption per kWh produced
Fuel price (diesel) | kr/l | 18.1 | Market price diesel per liter
Lifespan | hours | 43800 | Expected lifespan in operating hours
Annual maintenance cost | kr/yr | 25000 | Incl. oil change, filter, service
Other Settings
Parameter | Unit | Value | Comment
CO₂ factor methanol | kg CO₂/l | 1.088 | 44/32 × density 0.791
CO₂ factor diesel | kg CO₂/l | 2.68 | ADEME / IPCC standard
Assessment horizon | yr | 10 | Number of years for TCO comparison. Typically 1–10 years.
Solar Radiation – Monthly
Month | Unit | Solar Radiation (kWh/m²) | Comment
Jan | kWh/m² | 0.11065 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Feb | kWh/m² | 1.0208 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Mar | kWh/m² | 21.4439 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Apr | kWh/m² | 61.4387 | Enter expected solar radiation at location. Use PVGIS for an estimate.
May | kWh/m² | 79.3539 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Jun | kWh/m² | 79.3023 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Jul | kWh/m² | 80.6335 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Aug | kWh/m² | 71.4179 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Sep | kWh/m² | 37.7141 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Oct | kWh/m² | 3.0551 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Nov | kWh/m² | 0.25974 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Dec | kWh/m² | 0.01701 | Enter expected solar radiation at location. Use PVGIS for an estimate.
Note on B5: Author: Check coverage on Telenor coverage map (telenor.no/dekning). Yes = enables 4G-based communication and remote control.
Note on B6: Author: NB-IoT has better indoor coverage than 4G, but lower speed.
Note on B7: Author: Line of sight to gateway/base station within 15 km enables LoRaWAN.
Note on B8: Author: Two-way control requires 4G or satellite connection.
Note on B10: Author: Choose between: Pipe via intake, Pipe through dam, Gate/bottom valve, Notch in dam (V-profile).
Note on B11: Author: Yes = additional requirements for attraction water and up-/downstream migration (NVE Ch. 5).
Note on B12: Author: Specify minimum flow in l/s as stated in the concession.
Note on B13: Author: Yes = electromagnetic flow meter works poorly, use ultrasound or orifice plate.
Note on B14: Author: Yes = bubble tube or pressure cell recommended. Affects sensor selection and possible ice reduction.
Note on B19: Author: NVE requires min. 1 main inspection/year. ≤4 = 2 loggers.
Note on B21: Author: Yes = fuel cell (methanol) as secondary source. Higher fuel cost than diesel.
Note on C33: Author: Total system efficiency incl. losses in cables, MPPT, temperature and shading. Typically 75–85%.
Note on B39: Author: Specified as decimal: 0.8 = 80%. LiFePO4 typically tolerates 0.8–0.9.
Note on C45: Author: EFOY Pro 1800 average power. Source: SFC Energy datasheet.
Note on C48: Author: EFOY Pro 1800 typical lifespan. Source: SFC Energy datasheet.
Note on C60: Author: Stoichiometric: (44/32) × 0.791 kg/l. Source: Methanol Institute, 2022
Note on C61: Author: Source: ADEME / GHG Protocol / IPCC standard

## Power Budget
Power Budget – Equipment List
ON/OFF | Unit | Power (W) | Current Draw (A) | Consumption (Wh/day) | Current Draw (Ah/day) | Consumption (Wh/week) | Current Draw (Ah/week)
TRUE | Victron BMS | 0.1 | 0.0078125 | 2.4 | 0.1875 | 16.8 | 1.3125
TRUE | VICTRON Lynx Distributor | 2.4 | 0.1875 | 57.6 | 4.5 | 403.2 | 31.5
TRUE | VICTRON Orion TR Omformer DC-DC 12>24V 10A | 1.2 | 0.09375 | 28.8 | 2.25 | 201.6 | 15.75
TRUE | Victron Cerbo GX - MK2 | 2.8 | 0.21875 | 67.2 | 5.25 | 470.4 | 36.75
TRUE | VICTRON SmartSolar MPPT 250/100-TR VE.Can | 0.042 | 0.0032812 | 1.008 | 0.07875 | 7.056 | 0.55125
TRUE | Siemens FMS5020 | 6.45 | 0.50391 | 154.8 | 12.0938 | 1083.6 | 84.6562
TRUE | Teltonika RUT956 | 7 | 0.54688 | 168 | 13.125 | 1176 | 91.875
TRUE | Efoy Pro 1800 | 0.5 | 0.039062 | 12 | 0.9375 | 84 | 6.5625
TRUE | Efoy Fuel Manager FM4 | 0.0374 | 0.0029219 | 0.8976 | 0.070125 | 6.2832 | 0.49087
TRUE | Datalogger | 7 | 0.54688 | 168 | 13.125 | 1176 | 91.875
TRUE |  |  | 0 | 0 | 0 | 0 | 0
TRUE |  |  | 0 | 0 | 0 | 0 | 0
TRUE |  |  | 0 | 0 | 0 | 0 | 0
TRUE |  |  | 0 | 0 | 0 | 0 | 0
TRUE |  |  | 0 | 0 | 0 | 0 | 0
TRUE |  |  | 0 | 0 | 0 | 0 | 0
Total |  | 27.5294 | 2.1507 | 660.7056 | 51.6176 | 4624.9392 | 361.3234
Note on A2: Author: Use 1 for ON and 0 for OFF. Numeric values (not TRUE/FALSE) ensure compatibility across Office language settings.

## Results
RECOMMENDATION – Results and Energy Balance
Updated automatically from Input Data and Power Budget. Guidance – not definitive.
Recommended Configuration
Parameter | Unit | Comment
Measurement Method | Electromagnetic, orifice plate or ADP flow meter. Pressure cell, bubble tube, float or ultrasound/radar sensor | Select flow meter per recommended method
Communication | Satellite modem | Select modem/gateway based on coverage
Logger | 2 loggers + backup logger | See NVE requirements for specification
Energy Monitoring | No | Optional – requires 4G
Secondary Source | Diesel generator | Contact supplier
Secondary Source Power | 6500 | Contact supplier
Solar Panel (number of panels) | 2 | Select panel based on available area
Battery (Ah) | 500 | Manually specified battery bank
Fuel Consumption (l/yr) | 51.3 | Calculated from energy balance
Ice Adaptation | Standard
Operational Requirements | Straight run + laminar flow
NVE REQUIREMENTS (Guidelines for Hydrological Investigations)
Parameter | Value | Source
Measurement Frequency | Min. 1 time/hour | NVE requirement, determined by concession.
Accuracy | ±5 % | NVE requirement
Data Availability | Min. 97 % of the year | NVE requirement
Data Loggers and Water Level Sensor | 2 pcs (each) | NVE recommendation
Control Measurement | Every 3rd year | NVE requirement – calibration
Source: NVE Guide 3/2020 + Guidelines for Hydrological Investigations
Energy Balance – Annual Overview (Diesel generator)
Month | Days | Solar Panel Production (kWh) | Energy Balance (kWh) | Operating Time (h) | Fuel (l) | Fuel Cost (kr)
Jan | 31 | 0.075239 | -20.4066 | 3.1395 | 10.2033 | 184.68
Feb | 28 | 0.69415 | -17.8056 | 2.7393 | 8.9028 | 161.1407
Mar | 31 | 14.5818 | -5.9 | 0.9077 | 2.95 | 53.3954
Apr | 30 | 41.7783 | 21.9572 | 0 | 0 | 0
May | 31 | 53.9607 | 33.4788 | 0 | 0 | 0
Jun | 30 | 53.9256 | 34.1044 | 0 | 0 | 0
Jul | 31 | 54.8307 | 34.3489 | 0 | 0 | 0
Aug | 31 | 48.5642 | 28.0823 | 0 | 0 | 0
Sep | 30 | 25.6456 | 5.8244 | 0 | 0 | 0
Oct | 31 | 2.0774 | -18.4044 | 2.8315 | 9.2022 | 166.5601
Nov | 30 | 0.17662 | -19.6445 | 3.0222 | 9.8223 | 177.7831
Dec | 31 | 0.011567 | -20.4703 | 3.1493 | 10.2352 | 185.2563
SUM |  | 296.3219 | 55.1644 | 15.7895 | 51.3158 | 928.8157
Economics – Total Cost of Ownership (TCO)
Parameter | Unit | Fuel Cell (methanol) | Diesel Generator | Comment
Purchase | kr | 88000 | 35000 | Purchase price from supplier
Operating Cost/yr | kr/yr | 6927.6306 | 928.8157 | Fuel cost from energy balance
Maintenance/yr | kr/yr | 100 | 25000 | Annual maintenance from Input Data
Assessment Horizon | yr | 10 | 10 | Common time horizon from Input Data
TCO | kr | 158276.306 | 294288.1566 | Purchase + Horizon × (Operating + Maintenance) + possible replacement
Note on B9: Recommended secondary source. ≤ 3 inspections/year or desired zero-emission → fuel cell (methanol). Otherwise → diesel generator.
Note on B10: Power (W) for recommended secondary source. Diesel generator: from Input Data C53. Fuel cell: from Input Data C45.
Note on B11: Number of solar panels from Input Data. Panel area: quantity × 0.993 m²/panel.
Note on B12: Sized so the battery covers the power requirement for the desired number of autonomy days (without sun), adjusted for depth of discharge (DoD).
Note on B13: Summed annual fuel consumption from the energy balance. Only months with negative energy surplus contribute.
Note on A23: Author: Source: NVE, https://publikasjoner.nve.no/veileder/2020/veileder2020_03.pdf
Note on C26: Author: Monthly solar panel production. Solar radiation (from ArcGIS Pro in Input Data) × panel power × number of panels.
Note on D26: Author: Production minus consumption. Negative = deficit that must be covered by secondary source.
Note on E26: Hours the secondary source must run to cover the deficit. Deficit (kWh) / secondary source power (kW).
Note on F26: Liters of fuel (diesel or methanol) per month. Deficit (kWh) × consumption rate (l/kWh).
Note on G26: Author: Monthly fuel cost. Fuel (l) × price per liter for selected fuel type.
Note on C42: Author: Total cost for methanol fuel cell (EFOY type). Operating cost calculated independently of recommended source.
Note on D42: Author: Total cost for diesel generator. ★ = recommended secondary source based on inspection frequency and user selection.
Note on C44: Annual methanol fuel cost. Summed energy deficit × consumption rate × price per liter.
Note on D44: Annual diesel fuel cost. Summed energy deficit × consumption rate × price per liter.
Note on C45: Author: Annual maintenance cost for fuel cell, from Input Data.
Note on D45: Annual diesel maintenance cost, from Input Data.
Note on C46: From Input Data – common time horizon for comparison.
Note on D46: Diesel lifespan in years = operating hours / (annual energy demand from secondary source / diesel power). Uses diesel generator power (Input Data C55), not fuel cell power.
Note on C47: TCO = Purchase + Horizon × Annual Cost + replacement purchases. Fuel cell lifespan = Input Data C48 / own operating hours (independent of B9).
Note on D47: TCO = Purchase + Horizon × Annual Cost + replacement purchases. Diesel lifespan = Input Data C56 / own operating hours (independent of B9).